## Introduction
|  | Microbial barrier analysis | The Excel-calculation model is prepared by:
|  | Based on Norwegian Water report 202/2014 - Microbial barrier analysis (MBA) - a guideline (Ødegaard, et al.) | Asle Aasen, Bergen Vann Svein Forberg Liane, Norconsult Jon Brandt, Asplan Viak
The procedure is carried out by determining the following:
1 | The risk and vulnerability assessment of the system is based on:
| 1.1 | Raw water quality – giving us a starting point of the quality level
| 1.2 | Water utility size (the size of the water treatment plant)
| 1.3 | Type of water source (becomes important when determining necessary log-reduction)
2 | Point 1 determines the required barrier level, that must to be achieved to ensure an adequate hygienic barrier in the entire water treatment plant.
| 2.1 | The required barrier level is defined as the log-reduction in the three microorganism groups (bacteria, viruses and parasites) that must be achieved through barrier actions in the water treatment plant.
3 | "Log-credits" (reductions) may be given for the following actions:
| 3.1 | Barrier actions in catchment area and in the water source
| 3.2 | Water treatment actions beyond the final disinfection
| 3.3 | Improved monitoring and operation surveillance for the water source and water treatment plant
4 | By subtracting log-credits from the barrier level required, the log-reduction needed, in the final disinfection step or possible new extended water treatment process, may be determined.

## Start
Registration
Fill out the name of the water treatment plant and its owner:
Owner of water treatment plant: |  |  | BB
Name of the water treatment plant: |  |  | VV
It is assumed that the user of this Excel-based model is familiar with MBA report 202/2014.
Cells where values can /should be entered are highlighted in gray.
The model is mostly based on YES and NO questions. Predefined choices have been made in the model that appear as a possible selection, when the cursor is placed in a cell.
Determination of the required barrier level
Determine the necessary barrier level for water treatment plant, from its raw water source (water quality) and water treatment plants size. See figure and table below.
Required barrier level should be written in the cells bellow - and it is then transferred to the summary sheet:
Required barrier level
Bacteria | Viruses |  |  | Parasites
Raw water quality of a water source can be determined by using the table below (Table 2.2 from the report 202/2014). This is based on historical raw water quality data (see the figure above). If there is discharge of purified or uncleaned wastewater into the drinking water source, the source is directly categorized as category D (Da,Db or Dc). Along with the size of the water treatment plant, you find the necessary barrier level.
Size of water system
| A |  |  | B |  |  |  | C |  |  | D
| b | v | p | b | v | p |  | b | v | p | b | v | p
<1000 | 3 | 3 | 2 | 4 | 4 | 2 | a | 4.5 | 4.5 | 2.5 | 5 | 5 | 3
[7 empty] | b | 4.5 | 4.5 | 2.75 | 5 | 5 | 3.5
[7 empty] | c | 4.5 | 4.5 | 3 | 5 | 5 | 4
1000 - 10000 | 3.5 | 3.5 | 2.5 | 4.5 | 4.5 | 2.5 | a | 5 | 5 | 3 | 5.5 | 5.5 | 3.5
[7 empty] | b | 5 | 5 | 3.25 | 5.5 | 5.5 | 4
[7 empty] | c | 5 | 5 | 3.5 | 5.5 | 5.5 | 4.5
>10000 | 4 | 4 | 3 | 5 | 5 | 3 | a | 5.5 | 5.5 | 3.5 | 6 | 6 | 4
[7 empty] | b | 5.5 | 5.5 | 3.75 | 6 | 6 | 4.5
[7 empty] | c | 5.5 | 5.5 | 4 | 6 | 6 | 5

## Lakes and catchment areas
Owner of water treatment plant: |  | BB
Name of the water treatment plant: |  | VV
Log-credit for barrier actions in lakes and their catchment area. |  |  | Bacteria | Viruses | Parasites | Evaluation (Yes/No) | Bacteria | Viruses | Parasites
Log-credit for NEW physical and restrictive actions in lakes and catchment area (Table 2.4). | Reduction of the pollution load to the water source | Closing of all sewage discharges directly to the water source and to river systems that leads directly to the source | 0.75 | 0.75 | 0.5 | NO | 0 | 0 | 0
|  | Implementation of closed sewage systems (closed tank) for all sewage effluents in the catchment area, or watertight sewage systems bringing sewage out of the catchment area | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | Erecting fences for the prevention of farm animals, dogs stc. to come in direct contact with the source water and provision of garbage containers (including containers for dog feces) in the catchment area | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Restrictions in the activity allowed in the water source and the catchment area | Introducing a ban (or restrictions) on keeping grazing farm animals in the catchment area | 0.75 | 0.75 | 0.5 | NO | 0 | 0 | 0
|  | Introducing a ban on potentially polluting activities in the catchment area, e.g. homes, cottages, motor traffic, etc. | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
|  | Introducing a ban (or restrictions) on the use of watersports, bathing or other types of recreation in the water source, e.g. motor traffic | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Measures connected to the water intake in the lake | Lowering or moving of the water intake to a depth that ensures that the intake is below the thermocline except in the circulation periods | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | Moving the raw water intake to such a position that it can be documented through hydraulic studies that fecal pollution from sewage and animals does not affect the water quality at the intake | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Sum of log-credit for NEW actions in lakes and catchment area. (Absolute maximum summarized log-credit for barrier measures in water source and catchment are 2,0b + 2,0v + 1,25p.) | [5 empty] | 0 | 0 | 0
Log-credit for improved surveillance of the raw water quality (Table 2.7). | Increased sampling frequency | Extended microbial sampling and analysis program for raw water monitoring: at least as comprehensive as the risk-based program | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | Extended microbial sampling and analysis program for raw water monitoring: at least as comprehensive as that used for net control | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| On-line monitoring of raw water quality | On-line monitoring of raw water quality (turbidity, microbial activity or other parameters useful for monitoring the microbial quality), to be able to:
|  | - automatically close raw water supply | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | - manually close raw water supply | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
|  | - shift to another water source when exceeding the set point (alarm value) | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Absolute maximum summarized log-credit for improved sampling and on-line monitoring of raw water quality (Maximum summarized values are 0,75b + 0,75v + 0,50p.) | [5 empty] | 0 | 0 | 0
Sum of log credit for new actions in lakes and catchment area and sampling and on-line monitoring of raw water quality. (Maximum summarized values are 2,0b + 2,0v +1,25p.) Transfers to summary. | [6 empty] | 0 | 0 | 0

## Groundwater
Owner of water treatment plant: |  | BB
Name of the water treatment plant: |  | VV
Log-credit for barrier actions connected to groundwater |  |  | Bacteria | Viruses | Parasites | Evaluation (Yes/No) | Bacteria | Viruses | Parasites
Log-credit for NEW barrier actions connected to groundwater sources (Table 2.5) | Zone 0 The well zone | Fencing around and locking of gate to the well zone | 0.25 | 0.25 | 0.25 | NO | 0 | 0 | 0
| Zone 1 The close inflow zone. For groundwater in bedrock zone 1 extends to 100 m from the outer border of zone 0. | Introducing a ban on all forms of sewage installations in the zone. Including sewage pipes, septic tanks, on-site infiltration systems etc., as well as spreading of sewage sludge | 0.75 | 0.75 | 0.5 | NO | 0 | 0 | 0
|  | Introducing a ban on all form of agricultural activity including grass production, fertilizing, use of pesticides and use of the zone (or parts of it) as grazing land for farm animals | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | Introducing a ban on potentially polluting activities in the zone, e.g. homes, cottages, motor traffic etc. and all form of waste disposal sites | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Zone 2 The distant inflow zone. For groundwater in bedrock zone 2 extends to 100 m from the outer border of zone 1. | Introducing a ban on all forms of sewage discharges to the ground, including effluents that are infiltrated in the ground, spreading of sewage sludge etc. | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | Introducing a ban on all forms of agricultural activity in the zone, including grass production, fertilizing, use of pesticides and use of the zone (or parts of it) as grazing land for farm animals | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
|  | Introducing a ban on potentially polluting activities in the zone, e.g. homes, cottages, motor traffic etc. and all form of waste disposal sites | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Improvement of well design and construction | Protection of the well with a well-house with water-tight floor and sealing around the well pipe | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | For groundwater in bedrock: Complete sealing between casing and rock | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
|  | Raising of the well pipe to at least 40 cm above ground including a water-tight lid | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Absolut maximum summarized log-credit for barrier actions implemented in connection with ground water (Maximum summarized values are 2,0b + 2,0v + 1,25p.) | [5 empty] | 0 | 0 | 0
Log-credit for improved surveillance of the raw water quality (Table 2.7) | Increased sampling frequency | Extended microbial sampling and analysis program for raw water monitoring: at least as comprehensive as the risk-based program | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | Extended microbial sampling and analysis program for raw water monitoring: at least as comprehensive as that used for net control | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| On-line monitoring of raw water quality | On-line monitoring of raw water quality (turbidity, microbial activity or other parameters useful for monitoring the microbial quality), to be able to:
|  | - automatically close raw water supply | 0.5 | 0.5 | 0.25 | NO | 0 | 0 | 0
|  | - manually close raw water supply | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
|  | - shift to another water source when exceeding the set point (alarm value) | 0.25 | 0.25 | 0.15 | NO | 0 | 0 | 0
| Absolute maximum summarized log-credit for improved sampling and on-line monitoring of raw water quality (Maximum summarized values are 0.75b + 0.75v + 0.50p.) | [5 empty] | 0 | 0 | 0
Sum of log-credit for new actions connected to groundwater sources, sampling and on-line monitoring of raw water quality. (Maximum summarized values are 2,0b + 2,0v + 1,25p.) Transfers to summary. | [6 empty] | 0 | 0 | 0

## Infiltration
Owner of water treatment plant: | BB
Name of the water treatment plant: | VV
Artificial surface water infiltration improves the water quality depending on the water's residence time in the soil. The raw water quality is based on the quality of surface water and gives a specific log-credit for infiltration. This can also be used for natural infiltration of surface water into the soil. It is assumed that the residence time in the saturated and unsaturated zone can be determined by hydrogeological research.
Log-credit for water quality improvement through artificial infiltration of surface water (Table 2.6) |  |  | Bacteria | Viruses | Parasites | Evaluation (Yes/No) | Bacteria | Viruses | Parasites
Log-credit for artificial (or natural) surface water infiltration, based on the infiltrated water residence time in saturated and unsaturated zone. Select only one option from the YES/NO list. |  | > 60 days | 3 | 2.5 | 3 | NO | 0 | 0 | 0
|  | 30 - 60 days | 2.5 | 2 | 2.5 | NO | 0 | 0 | 0
|  | 15 - 30 days | 2 | 1.5 | 2 | NO | 0 | 0 | 0
|  | 3 - 15 days | 1.5 | 1 | 1.5 | NO | 0 | 0 | 0
Log-credit for infiltration of surface water. Transfers to summary. | [6 empty] | 0 | 0 | 0

## WT beyond disinf. (process 1)
Owner of water treatment plant: |  | BB
Name of the water treatment plant: |  | VV
Log-credit for water treatment measures beyond final disinfection |  |  | Bacteria | Viruses | Parasites | Evaluation (Yes/No) | Bacteria | Viruses | Parasites
Log-credit for particle separation processes in water treatment (Table 2.8) | Rapid sand filtration without coagulation < 7,5 m/h (also valid for: biofilters, ion exchange filters, activated carbon filters and calcium carbonate filters) |  | 0.5 | 0.25 | 0.5 | NO | 0 | 0 | 0
| Micro membrane (MF) filtration - nominal membrane pore diameter < 100 nm |  | 2 | 1 | 2 | NO | 0 | 0 | 0
| Ultra membrane (UF) filtration - nominal membrane pore diameter < 40 nm |  | 2.5 | 2 | 2.5 | NO | 0 | 0 | 0
| Nano membrane (NF) filtration -nominal membrane pore diameter < 5 nm |  | 3 | 3 | 3 | NO | 0 | 0 | 0
| Slow sand filtration - filtration rate < 0,5 m/h |  | 2 | 2 | 2 | NO | 0 | 0 | 0
| Coagulation - direct filtration (media-filter) - provided turbidity in produced water < 0,2 NTU |  | 2.25 | 1.5 | 2.25 | NO | 0 | 0 | 0
| Coagulation - direct filtration (media-filter) - provided turbidity in produced water < 0,1 NTU |  | 2.5 | 2 | 2.5 | NO | 0 | 0 | 0
| Coagulation + sedimentation (or flotation) + filtration - provided turbidity in produced water < 0,2 NTU |  | 2.5 | 1.75 | 2.5 | NO | 0 | 0 | 0
| Coagulation + sedimentation (or flotation) + filtration - provided turbidity in produced water < 0,1 NTU |  | 2.75 | 2.25 | 2.75 | NO | 0 | 0 | 0
| Coagulation - micro membrane (MF) filtration - provided turbidity in produced water < 0,1 NTU |  | 3 | 2.5 | 3 | NO | 0 | 0 | 0
| Coagulation - Ultra membrane (UF) filtration - provided turbidity in produced water < 0,1 NTU |  | 3 | 3 | 3 | NO | 0 | 0 | 0
| Determination of log-credit for particle separation processes in water treatment. | [5 empty] | 0 | 0 | 0
Deduction of the log-credit for lack of operation control monitoring actions (Table 2.9) | On-line monitoring of treated water quality with follow-up actions to comply with set limit values | For on-line monitoring of treated water turbidity, color or other parameter suitable for process control: (NOTE! Only one of the following alternatives in the list below can be chosen) |  |  |  |  | Bacteria | Viruses | Parasites
|  | a) is lacking |  |  | 40% | NO | 0 | 0 | 0
|  | b) is present, activating an alarm when over-shooting a set-point (alarm value) leading to manual correction of process conditions (e.g. adjustments of pH, coagulant dose etc.) so that normal operation is restored |  |  | 20% | NO | 0 | 0 | 0
|  | c) is present, activating an alarm when over-shooting a set-point (alarm value) leading to manual closing of raw water supply until the cause of abnormality is found and normal operation is restored |  |  | 10% | NO | 0 | 0 | 0
|  | d) is present, activating an alarm when over-shooting a set-point (alarm value) leading to automatic closing of raw water supply until the cause of abnormality is found and normal operation is restored |  |  | 0% | NO | 0 | 0 | 0
| Continuous monitoring of the electricity supply with follow-up actions at lapse of electricity supply | If continuous monitoring and data transmitting to a control central of electricity supply data: (NOTE! Only one of the following alternatives in the list below can be chosen)
|  | a) is lacking |  |  | 40% | NO | 0 | 0 | 0
|  | b) is present, activating an alarm at lapse of electricity supply, leading to manual closing of raw water supply, until normal electricity supply is restored |  |  | 20% | NO | 0 | 0 | 0
|  | c) is present, activating an alarm at lapse of electricity supply, leading to automatic closing of raw water supply, until normal electricity supply is restored |  |  | 0% | NO | 0 | 0 | 0
|  | d) is present, activating an alarm leading to manual start-up of emergency el-supply generator and/or UPS at failure of electricity supply |  |  | 20% | NO | 0 | 0 | 0
|  | e) is present, activating an alarm leading to automatic start-up of emergency el-supply generator and/or UPS at failure of electricity supply |  |  | 0% | NO | 0 | 0 | 0
Log-credit for measures in water treatment plants with particle separation process, including any deductions for deficiencies in operational monitoring. Transfers to summary. | [6 empty] | 0 | 0 | 0
Note on C19: Aasen, Asle: Grenseverdiene må fastsettes for den relevante parameter i hvert enkelt tilfelle

## WT beyond disinf. (process 2)
Owner of water treatment plant: |  | BB
Name of the water treatment plant: |  | VV
This side can be used if water treatment plant has more than one water treatment process for particle separation. This is than used for water treatment process/step 2.
Log-credit for water treatment measures beyond final disinfection |  |  | Bacteria | Viruses | Parasites | Evaluation (Yes/No) | Bacteria | Viruses | Parasites
Log-credit for particle separation processes in water treatment (Table 2.8) | Rapid sand filtration without coagulation < 7,5 m/h (also valid for: biofilters, ion exchange filters, activated carbon filters and calcium carbonate filters) |  | 0.5 | 0.25 | 0.5 | NO | 0 | 0 | 0
| Micro membrane (MF) filtration - nominal membrane pore diameter < 100 nm |  | 2 | 1 | 2 | NO | 0 | 0 | 0
| Ultra membrane (UF) filtration - nominal membrane pore diameter < 40 nm |  | 2.5 | 2 | 2.5 | NO | 0 | 0 | 0
| Nano membrane (NF) filtration -nominal membrane pore diameter < 5 nm |  | 3 | 3 | 3 | NO | 0 | 0 | 0
| Slow sand filtration - filtration rate < 0,5 m/h |  | 2 | 2 | 2 | NO | 0 | 0 | 0
| Coagulation - direct filtration (media-filter) - provided turbidity in produced water < 0,2 NTU |  | 2.25 | 1.5 | 2.25 | NO | 0 | 0 | 0
| Coagulation - direct filtration (media-filter) - provided turbidity in produced water < 0,1 NTU |  | 2.5 | 2 | 2.5 | NO | 0 | 0 | 0
| Coagulation + sedimentation (or flotation) + filtration - provided turbidity in produced water < 0,2 NTU |  | 2.5 | 1.75 | 2.5 | NO | 0 | 0 | 0
| Coagulation + sedimentation (or flotation) + filtration - provided turbidity in produced water < 0,1 NTU |  | 2.75 | 2.25 | 2.75 | NO | 0 | 0 | 0
| Coagulation - micro membrane (MF) filtration - provided turbidity in produced water < 0,1 NTU |  | 3 | 2.5 | 3 | NO | 0 | 0 | 0
| Coagulation - Ultra membrane (UF) filtration - provided turbidity in produced water < 0,1 NTU |  | 3 | 3 | 3 | NO | 0 | 0 | 0
| Determination of log-credit for particle separation processes in water treatment. | [5 empty] | 0 | 0 | 0
Deduction of the log-credit for lack of operationcontrol monitoring actions (Table 2.9) | On-line monitoring of treated water quality with follow-up actions to comply with set limit values | For on-line monitoring of treated water turbidity, color or other parameter suitable for process control: (NOTE! Only one of the following alternatives in the list below can be chosen) |  |  |  |  | Bacteria | Viruses | Parasites
|  | a) is lacking |  |  | 40% | NO | 0 | 0 | 0
|  | b) is present, activating an alarm when over-shooting a set-point (alarm value) leading to manual correction of process conditions (e.g. adjustments of pH, coagulant dose etc.) so that normal operation is restored |  |  | 20% | NO | 0 | 0 | 0
|  | c) is present, activating an alarm when over-shooting a set-point (alarm value) leading to manual closing of raw water supply until the cause of abnormality is found and normal operation is restored |  |  | 10% | NO | 0 | 0 | 0
|  | d) is present, activating an alarm when over-shooting a set-point (alarm value) leading to automatic closing of raw water supply until the cause of abnormality is found and normal operation is restored |  |  | 0% | NO | 0 | 0 | 0
| Continuous monitoring of the electricity supply with follow-up actions at lapse of electricity supply | If continuous monitoring and data transmitting to a control central of electricity supply data: (NOTE! Only one of the following alternatives in the list below can be chosen)
|  | a) is lacking |  |  | 40% | NO | 0 | 0 | 0
|  | b) is present, activating an alarm at lapse of electricity supply, leading to manual closing of raw water supply, until normal electricity supply is restored |  |  | 20% | NO | 0 | 0 | 0
|  | c) is present, activating an alarm at lapse of electricity supply, leading to automatic closing of raw water supply, until normal electricity supply is restored |  |  | 0% | NO | 0 | 0 | 0
|  | d) is present, activating an alarm leading to manual start-up of emergency el-supply generator and/or UPS at failure of electricity supply |  |  | 20% | NO | 0 | 0 | 0
|  | e) is present, activating an alarm leading to automatic start-up of emergency el-supply generator and/or UPS at failure of electricity supply |  |  | 0% | NO | 0 | 0 | 0
Log-credit for measures in water treatment plants with particle separation process, including any deductions for deficiencies in operational monitoring. Transfers to summary. | [6 empty] | 0 | 0 | 0
Note on C21: Aasen, Asle: Grenseverdiene må fastsettes for den relevante parameter i hvert enkelt tilfelle

## UV
Owner of water treatment plant: |  | BB
Name of the water treatment plant: |  | VV
Log-credit for UV-disinfection
Maximum log-reduction for approved UV plants at varying UV-dose: |  | Bacteria | Virus excl. Adenovirus | Virus based on Adenovirus | Parasites
UV-dose 40 mJ/cm2 determined biodosimetrically |  | 4 | 3.5 | 1.25 | 4
UV-dose 30 mJ/cm2 calculated biodosimetrically |  | 3 | 2.5 | 0.75 | 3
Special cases (Table 3.9): |  | Bacteria | Virus excl. Adenovirus | Virus based on Adenovirus | Parasites
UV-dose 30 mJ/cm2 determined biodosimetrically |  | 3.5 | 3 | 1 | 3.5
UV-dose 25 mJ/cm2 calculated biodosimetrically |  | 3 | 2.5 | 0.75 | 3
Select the category for maximum disabling UV disinfection in the drop-down menu below (by placing your arrow in the cell below you will get the help menu): |  | Bacteria | Virus excl. Adenovirus | Virus based on Adenovirus | Parasites
Does not have UV disinfection |  | 0 | 0 | 0 | 0
Reduction in log-credit for UV-disinfection (in % of maximum log-reduction) because of safety breaches for various main categories of barrier actions, as well as credit (in % of maximum log-reduction) for measures actually implemented in each category (Table 3.10):
A | Actions for temporary failure or reduced effect of the UV-irradiation: |  |  | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Viruses | Parasites | Bacteria | Viruses | Parasites
| Lack of actions provides maximum deduction of: |  | 10% |  |  | 0 | 0 | 0 | 0 | 0 | 0
A1 | Automatic shutting down of all water production (requires sufficient equalizing volume in the system) |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
A2 | Alarm and automatic start-up of reserve disinfection - for instance chlorination facility |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
| Maximum deduction in category A | [7 empty] | 0 | 0 | 0
B | Actions to reduce the risk of temporary failure or reduced effect of the UV-irradiation: |  |  |  |  | Bacteria | Viruses | Parasites | Bacteria | Viruses | Parasites
| Lack of actions provides maximum deduction of: |  | 20% |  |  | 0 | 0 | 0 | 0 | 0 | 0
B1 | UPS installed |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
B2 | Back-up generator installed |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
B3 | Documentation of good and reliable power supply |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
| Maximum deduction in category B | [7 empty] | 0 | 0 | 0
C | Other design related issues: |  |  |  |  | Bacteria | Viruses | Parasites | Bacteria | Viruses | Parasites
| Lack of actions provides maximum deduction of: |  | 30% |  |  | 0 | 0 | 0 | 0 | 0 | 0
C1 | Several UV-reactors designed and installed in such a way that full supply may be maintained at lapse of one |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
C2 | Separate flow measurement for each UV-reactor to secure good hydraulic control |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
C3 | Control sensors (UV intensity, UV-transmission etc.) correctly located |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
C4 | Equalization volume located after UV-plant |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
C5 | Reserve disinfection plant installed for instance chlorination facility |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
| Maximum deduction in category C | [7 empty] | 0 | 0 | 0
D | Other operation related issues: |  |  |  |  | Bacteria | Viruses | Parasites | Bacteria | Viruses | Parasites
| Lack of actions provides maximum deduction of: |  | 30% |  |  | 0 | 0 | 0 | 0 | 0 | 0
D1 | A storage of critical reserve equipment (quartz-pipes, lamps, o-rings, wipers, wiper driving gear, ballasts, ballast fan, UV sensors and UV-transmissions sensors) |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
D2 | Automatic shutting down of all water production if operation in connection with start-up |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
D3 | Good dose control |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
D4 | Automatic shutting down of all water production if operation is outside validation range |  | 10% | NO | 0% |  |  |  | 0 | 0 | 0
D5 | Alarm if the operation is outside validation range |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
D6 | Satisfactory routines for cleaning, control and calibration of sensors |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
D7 | Documentation of operation in terms of duration curves (curves that display calculated dose as a function of time) |  | 5% | NO | 0% |  |  |  | 0 | 0 | 0
| Maximum deduction in category D | [7 empty] | 0 | 0 | 0
|  |  |  | Reduced inactivation rate because of missing implemented measures: |  |  |  |  | 0 | 0 | 0
If UV-transmission of incoming water is lower than UV-plant is designed for, the log reduction shall be reduced (Figure 3.6):
UV-units designed UV-transmission per. 5 cm (UVT50)
UV-transmission per. 5 cm of incoming water / water after failure in previous particle removal step (UVT50)
According to Figure 3.6, this gives a reduction factor of:
|  |  |  | Log-credit for UV-disinfection including deductions. Transfers to summary. |  |  |  |  | 0 | 0 | 0
Figure 3.6 Reduction (in %) of calculated log-credit for UV-disinfection because of low UV-transmission in incoming water to UV plant and UV-transmission design.
The deduction in log-credit can be avoided, if the amount of water that is supplied to the UV-plant is reduced to the point, where the increased UV-dose used results in a sustainable log-reduction, when the upstream treatments, that are supposed to improve the transmission, are out of operation. If the water production is shut down automatically, when the operating conditions in the UV-plant are outside of the operating range that the UV-plant is certified for, then no deduction in log-credit shall be done.

## Chlorine
| Owner of water treatment plant: |  | BB
| Name of the water treatment plant: |  | VV
Log-credit for Chlorine-disinfection
| Select conditions for disinfection from the dropdown menu below (by placing the arrow in the cell below you will get the help menu): |  |  | Bacteria | Virus | Giardia | Cryptosporidium
|  |  |  | 3 log | 3 log | 2 log | 2 log
| Does not disinfect with chlorine |  |  | 0 | 0 | 0 | 0
Input data: This is information about own operations that are taken in consideration to be able to perform calculations
| Enter TOC value in the water being chlorinated - highest value | [5 empty] | mg TOC/l
| Enter normal chlorine dosage (Cdose) | [5 empty] | mg Cl2/l
| Enter event. measured residual chlorine level after chlorine contact tank (Cut) | [5 empty] | mg Cl2/l
| Enter event. measured chlorine level at inlet to chlorine contact tank (Cin) | [5 empty] | mg Cl2/l
| Enter theoretical residence time in the chlorine contact tank (T = Q/V) | [5 empty] | minutes
Required Ct-values (mg·min/l) for inactivation of bacteria, virus and parasites (Table 3.1)
| CHLORINE | Bacteria |  | Virus |  | Parasites of the |  | Parasites of the
[6 empty] | Giardia group |  | Cryptosporidium group
|  | (3 log) |  | (3 log) |  | (2 log) |  | (2 log)
|  | 4oC | 0,5 oC | 4oC | 0,5oC | 4oC | 0,5oC | 4oC | 0,5oC
| pH < 7 | 1 | 1.5 | 4 | 6 | 75 | 100 | n.s. | n.s.
| pH 7 – 8 | 1.5 | 2 | 6 | 9 | 100 | 150 | n.s. | n.s.
| pH > 8 | 2 | 3 | 8 | 12 | 175 | 250 | n.s. | n.s.
n.s. - not stated. The Ct-value is si high that it is of no interest for all practical purposes
Recommended values for hydraulic factor and serial factor at various mixing conditions (Table 3.2). Chose YES for selected mixing condition and description of each chamber in contact tank:
| Mixing condition (extent of plug flow (PF) in each chamber | Select (only one option) | Hydraulic factor Fh |  | Description of each chamber in contact tank |  |  | Serial factor Fs
Chambers in series (only one option)
|  |  | t10/T1) | tm/T2) |  |  |  | 1 |  | 2 |  | 3
| No PF (complete mixing) |  | 0.1 | 0.3 | No baffles, agitated tank, high in- and out- velocities, low length/width ratio in tank (≤1) |  |  |  | 1 |  | 2 |  | 2.5
| Poor PF |  | 0.3 | 0.4 | No baffles inside tank, single or multiple inlets and outlets in tank, length/width ratio in tank > 1 |  |  |  | 1 |  | 1.8 |  | 2
| Average PF |  | 0.5 | 0.5 | Baffled inlet or outlet, some baffles inside tank and possibly multiple inlets and outlets. Length/width ratio in tank >4. |  |  |  | 1 |  | 1.5 |  | 1.8
| Quite good PF |  | 0.7 | 0.7 | Baffled inlet serpentine baffles inside tank to increase length/width ratio to >6. |  |  |  | 1 |  | 1.3 |  | 1.4
| Very good PF |  | 0.9 | 0.9 | 1) To be used in Ct-calcul+C45:E46ation (see secti+G36on 3.7.4 in the report 202/2014) |  |  |  | 1 |  | 1.1 |  | 1.1
| Perfect PF |  | 1 | 1 | Very high length/width ratio (>20). Pipeline flow |  |  |  | 1 |  | 1 |  | 1
1) To be used in Ct-calculation (see section 3.7.4 in the report 202/2014)
2) To be used in calculation of k, Ci, Cout (see section 3.4.2 and section 3.7.2-3.7.3 in the report 202/2014)
Effective residence time in the chlorine contact tank (calculated from the table 3.2 and theoretical residence time)
| Hydraulic factor, Fh based on t10/T |  |  | Must enter a value!
| Hydraulic factor, Fh based on tm/T |  |  | Must enter a value!
| Serial factor, Fs |  |  | Must enter a value!
| Theoretical residence time, T=Q/V (min) |  |  | 0
| Effective residence time teff based on t10/T |  |  | Chose mixing condition
| Effective residence time teff based on tm/T |  |  | Chose mixing condition
Chose a method to calculate the Ct-value by using the dropdown menu (placing the arrow in the gray cell brings up the dropdown menu):
| Method to determine the IC and k |  | through model calculation (Cdose, TOC)
Calculated values
| IC (initial consumption) * | mg Cl2/l | #DIV/0!
| Cin | mg Cl2/l | #DIV/0!
| k (degradation constant) |  | #DIV/0!
| Ct-value | mg*min/l | #DIV/0! | (teff based on t10/T)
* If both chlorine and chlorine dioxide is used for disinfection, the initial consumption (IC) must be adjusted as follows:
ICchlorine, adjusted = (Cdose, chlorine / (Cdose, chlorine dioxide + Cdose, chlorine)) x ICchlorine
Log-credit for chlorine disinfection before potential deductions
|  |  | Bacteria | Virus | Giardia | Cryptosporidium
| Maximum log-credit |  | 4 | 4 | 3 | 3
| Calculated inactivation degree (log-reduction) |  | 0 | 0 | 0 | 0
| Used log-credit before deduction |  | 0 | 0 | 0 | 0
Deduction (in %) of the Ct-calculated (or maximum) log-reduction because of safety breaches in chemical disinfection plants as well as credit (in % of log-reduction) for safety actions actually implemented (Table 3.7):
A | Action at temporary dosing failure | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 10% |  |  | 0 | 0 | 0 | 0
A1 | Automatic shutdown of all water production | 10% | NO | 10% | 0 | 0 | 0 | 0
A2 | Alarm and automatic start of dosing equipment in reserve | 5% | NO | 5% | 0 | 0 | 0 | 0
Maximum deduction in category A: |  |  |  |  | 0 | 0 | 0 | 0
B | Action to reduce risk of dosing failure | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 15% |  |  | 0 | 0 | 0 | 0
B1 | Back-up generator and/or UPS installed | 10% | NO | 10% | 0 | 0 | 0 | 0
B2 | Reserve dosing equipment installed | 5% | NO | 5% | 0 | 0 | 0 | 0
B3 | Equalization volume that may satisfy the water need when water production is stopped at dosing failures | 10% | NO | 10% | 0 | 0 | 0 | 0
Maximum deduction in category B: |  |  |  |  | 0 | 0 | 0 | 0
C | Other actions | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 10% |  |  | 0 | 0 | 0 | 0
C1 | Satisfactory monitoring system installed | 5% | NO | 5% | 0 | 0 | 0 | 0
C2 | Storage of critical reserve equipment | 5% | NO | 5% | 0 | 0 | 0 | 0
C3 | Satisfactory routines for cleaning, control and calibration of sensors for monitoring of residual chlorine | 5% | NO | 5% | 0 | 0 | 0 | 0
Maximum deduction in category C: |  |  |  |  | 0 | 0 | 0 | 0
Log-reduction when using chlorine disinfection method: |  |  |  |  | Bacteria | Virus | Giardia | Cryptosporidium
Log-credit before deduction: |  |  |  |  | 0 | 0 | 0 | 0
Reduction in log-credit because or missing actions (A + B + C): |  |  |  |  | 0 | 0 | 0 | 0
Log-credit for chlorine disinfection including deductions. Transfers to summary. |  |  |  |  | 0 | 0 | 0 | 0

## Chlorine dioxide
| Owner of water treatment plant: |  | BB
| Name of the water treatment plant: |  | VV
Log-credit for Chlorine dioxide-disinfection
| Select conditions for disinfection from the dropdown menu below (by placing the arrow in the cell below you will get the help menu): |  |  | Bacteria | Virus | Giardia | Cryptosporidium
|  |  |  | 3 log | 3 log | 2 log | 2 log
| Does not disinfect with chlorine dioxide |  |  | 0 | 0 | 0 | 0
Input data: This is information about own operations that are taken in consideration to be able to perform calculations
| Enter TOC value in the water being chlorinated - highest value | [5 empty] | mg TOC/l
| Enter normal chlorine dosage (Cdose) | [5 empty] | mg Cl2/l
| Enter event. measured residual chlorine level after chlorine contact tank (Cout) | [5 empty] | mg Cl2/l
| Enter event. measured chlorine level at inlet to chlorine contact tank (Cin) | [5 empty] | mg Cl2/l
| Enter theoretical residence time in the chlorine contact tank (T = Q/V) | [5 empty] | minutes
Required Ct-values (mg·min/l) for inactivation of bacteria, virus and parasites (Table 3.1)
|  | Bacteria |  | Virus |  | Parasites of the |  | Parasites of the
[6 empty] | Giardia group |  | Cryptosporidium group
|  | (3 log) |  | (3 log) |  | (2 log) |  | (2 log)
|  | 4oC | 0,5 oC | 4oC | 0,5oC | 4oC | 0,5oC | 4oC | 0,5oC
| Chlorine dioxide | 1 | 1.5 | 10 | 15 | 20 | 30 | >100 | >150
Recommended values for hydraulic factor and serial factor at various mixing conditions (Table 3.2). Chose YES for selected mixing condition and description of each chamber in contact tank:
| Mixing condition (extent of plug flow (PF) in each chamber | Select (only one option) | Hydraulic factor Fh |  | Description of each chamber in contact tank |  |  | Serial factor Fs
Chambers in series (only one option)
|  |  | t10/T1) | tm/T2) |  |  |  | 1 |  | 2 |  | 3
| No PF (complete mixing) |  | 0.1 | 0.3 | No baffles, agitated tank, high in- and out- velocities, low length/width ratio in tank (≤1) |  |  |  | 1 |  | 2 |  | 2.5
| Poor PF |  | 0.3 | 0.4 | No baffles inside tank, single or multiple inlets and outlets in tank, length/width ratio in tank > 1 |  |  |  | 1 |  | 1.8 |  | 2
| Average PF |  | 0.5 | 0.5 | Baffled inlet or outlet, some baffles inside tank and possibly multiple inlets and outlets. Length/width ratio in tank >4. |  |  |  | 1 |  | 1.5 |  | 1.8
| Quite good PF |  | 0.7 | 0.7 | Baffled inlet serpentine baffles inside tank to increase length/width ratio to >6. |  |  |  | 1 |  | 1.3 |  | 1.4
| Very good PF |  | 0.9 | 0.9 | Baffled inlet, serpentine or perforated plate baffles inside tank. High length/width ratio (>10). |  |  |  | 1 |  | 1.1 |  | 1.1
| Perfect PF |  | 1 | 1 | Very high length/width ratio (>20). Pipeline flow |  |  |  | 1 |  | 1 |  | 1
1) To be used in Ct-calculation (see section 3.7.4 in the report 202/2014)
2) To be used in calculation of k, Ci, Cout (see section 3.4.2 and section 3.7.2-3.7.3 in the report 202/2014)
Effective residence time in the chlorine contact tank (calculated from the table 3.2 and theoretical residence time)
| Hydraulic factor, Fh based on t10/T |  |  | Must enter a value!
| Hydraulic factor, Fh based on tm/T |  |  | Must enter a value!
| Serial factor, Fs |  |  | Must enter a value!
| Theoretical residence time, T=Q/V (min) |  |  | 0
| Effective residence time teff based on t10/T |  |  | Chose mixing condition!
| Effective residence time teff based on tm/T |  |  | Chose mixing condition!
Chose a method to calculate the Ct-value by using the dropdown menu (placing the arrow in the gray cell brings up the dropdown menu):
| Method to determine the IC and k |  | through a combination of measurements and calculations (Cdose, Cout og TOC)
Calculated values
| IC (initial consumption) * | mg Cl2/l | #DIV/0!
| Cin | mg Cl2/l | #DIV/0!
| k (degradation constant) |  | #DIV/0!
| Ct-value | mg*min/l | #DIV/0! | (teff based on t10/T)
* If both chlorine and chlorine dioxide is used for disinfection, the initial consumption (IC) must be adjusted as follows:
ICChlorine dioxide, adjusted = (Cdose, Chlorine dioxide / (Cdose, Chlorine dioxide + Cdose, Chlorine)) x ICChlorine dioxide
Log-credit for chlorine dioxide disinfection before potential deductions
|  |  | Bacteria | Virus | Giardia | Crypto-sporidium
| Maximum log-credit |  | 4 | 4 | 3 | 3
| Calculated inactivation degree (log-reduction) |  | 0 | 0 | 0 | 0
| Used log-credit before deduction |  | 0 | 0 | 0 | 0
Deduction (in %) of the Ct-calculated (or maximum) log-reduction because of safety breaches in chemical disinfection plants as well as credit (in % of log-reduction) for safety actions actually implemented (Table 3.7):
A | Action at temporary dosing failure | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 10% |  |  | 0 | 0 | 0 | 0
A1 | Automatic shutdown of all water production | 10% | NO | 0% | 0 | 0 | 0 | 0
A2 | Alarm and automatic start of dosing equipment in reserve | 5% | NO | 0% | 0 | 0 | 0 | 0
Maximum deduction in category A: |  |  |  |  | 0 | 0 | 0 | 0
B | Action to reduce risk of dosing failure | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 15% |  |  | 0 | 0 | 0 | 0
B1 | Back-up generator and/or UPS installed | 10% | NO | 0% | 0 | 0 | 0 | 0
B2 | Reserve dosing equipment installed | 5% | NO | 0% | 0 | 0 | 0 | 0
B3 | Equalization volume that may satisfy the water need when water production is stopped at dosing failures | 10% | NO | 0% | 0 | 0 | 0 | 0
Maximum deduction in category B: |  |  |  |  | 0 | 0 | 0 | 0
C | Other actions | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 10% |  |  | 0 | 0 | 0 | 0
C1 | Satisfactory monitoring system installed | 5% | NO | 0% | 0 | 0 | 0 | 0
C2 | Storage of critical reserve equipment | 5% | NO | 0% | 0 | 0 | 0 | 0
C3 | Satisfactory routines for cleaning, control and calibration of sensors for monitoring of residual chlorine | 5% | NO | 0% | 0 | 0 | 0 | 0
Maximum deduction in category C: |  |  |  |  | 0 | 0 | 0 | 0
Log-reduction when using chlorine dioxide disinfection method: |  |  |  |  | Bacteria | Virus | Giardia | Cryptosporidium
Log-credit before deduction: |  |  |  |  | 0 | 0 | 0 | 0
Reduction in log-credit because or missing actions (A + B + C): |  |  |  |  | 0 | 0 | 0 | 0
Log-credit for chlorine dioxide disinfection including deductions. Transfers to summary. |  |  |  |  | 0 | 0 | 0 | 0

## Ozone
| Owner of water treatment plant: |  | BB
| Name of the water treatment plant: |  | VV
Log-credit for Ozone-disinfection
| Select conditions for disinfection from the dropdown menu below (by placing the arrow in the cell below you will get the help menu): |  |  | Bacteria | Virus | Giardia | Cryptosporidium
|  |  |  | 3 log | 3 log | 2 log | 2 log
| Does not disinfect with ozone |  |  | 0 | 0 | 0 | 0
Input data: This is information about own operations that are taken in consideration to be able to perform calculations
Enter pH value in the water being treated with ozone - normal value
| Enter TOC value in the water being treated with ozone - highest value | [5 empty] | mg TOC/l
| Enter ozone dosage (Cdose) | [5 empty] | mg O3/l
Enter ozone transfer constant (ktransfer) - See the table below *
| Enter event. measured residual ozone level after ozone reaction chamber (Cout) | [5 empty] | mg O3/l
| Enter event. measured chlorine level at inlet to ozone reaction chamber (Cin) | [5 empty] | mg O3/l
| Enter theoretical residence time in the ozone reaction chamber (T = Q/V) | [5 empty] | minutes
* Recommended values for the ozone transfer constant, ktransfer.
| Contacting system |  | ktransfer
| Diffuser/injector mixing, packed contact tank |  | 0.9
| Diffuser/injector mixing, contact tank without packing |  | 0.75
| Injector mixing in pipe proceeded by closed ppeline contact tank |  | 0.99
Required Ct-values (mg·min/l) for inactivation of bacteria, virus and parasites (Table 3.1)
|  | Bacteria |  | Virus |  | Parasites of the |  | Parasites of the
[6 empty] | Giardia group |  | Cryptosporidium group
|  | (3 log) |  | (3 log) |  | (2 log) |  | (2 log)
|  | 4oC | 0,5 oC | 4oC | 0,5oC | 4oC | 0,5oC | 4oC | 0,5oC
| Ozone | 0.5 | 0.75 | 1 | 1.4 | 1.5 | 2 | 30 | 45
Recommended values for hydraulic factor and serial factor at various mixing conditions (Table 3.2 and 3.3). Chose YES for selected mixing condition and description of each chamber in contact tank:
| Mixing condition (extent of plug flow (PF) in each chamber | Select (only one option) | Hydraulic factor Fh |  | Description of each chamber in contact tank |  |  | Serial factor Fs
Chambers in series (only one option)
|  |  | t10/T1) | tm/T2) |  |  |  | 1 |  | 2 |  | 3
| No PF (complete mixing) |  | 0.1 | 0.3 | No baffles, agitated tank, high in- and out- velocities, low length/width ratio in tank (≤1) |  |  |  | 1 |  | 2 |  | 2.5
| Poor PF |  | 0.3 | 0.4 | No baffles inside tank, single or multiple inlets and outlets in tank, length/width ratio in tank > 1 |  |  |  | 1 |  | 1.8 |  | 2
| Average PF |  | 0.5 | 0.5 | Baffled inlet or outlet, some baffles inside tank and possibly multiple inlets and outlets. Length/width ratio in tank >4. |  |  |  | 1 |  | 1.5 |  | 1.8
| Quite good PF |  | 0.7 | 0.7 | Baffled inlet serpentine baffles inside tank to increase length/width ratio to >6. |  |  |  | 1 |  | 1.3 |  | 1.4
| Very good PF |  | 0.9 | 0.9 | Baffled inlet, serpentine or perforated plate baffles inside tank. High length/width ratio (>10). |  |  |  | 1 |  | 1.1 |  | 1.1
| Perfect PF |  | 1 | 1 | Very high length/width ratio (>20). Pipeline flow |  |  |  | 1 |  | 1 |  | 1
| Open columns- With gas bubbles present |  | 0.5 | 0.55 |  |  |  |  | 1 |  | 1.5 |  | 1.8
| Open columns- Without gas bubbles present |  | 0.7 | 0.75 |  |  |  |  | 1 |  | 1.3 |  | 1.4
| Packed columns- With gas bubbles present |  | 0.85 | 0.85 |  |  |  |  | 1 |  | 1.1 |  | 1.1
| Packed columns- Without gas bubbles present |  | 0.95 | 0.95 |  |  |  |  | 1 |  | 1 |  | 1
1) To be used in Ct-calculation (see section 3.7.4 in the report 202/2014)
2) To be used in calculation of k, Ci, Cout (see section 3.4.2 and section 3.7.2-3.7.3 in the report 202/2014)
Effective residence time in the ozone reaction chamber (calculated from the table 3.2 and theoretical residence time)
| Hydraulic factor, Fh based on t10/T |  |  | Must enter a value!
| Hydraulic factor, Fh based on tm/T |  |  | Must enter a value!
| Serial factor, Fs |  |  | Must enter a value!
| Theoretical residence time, T=Q/V (min) |  |  | 0
| Effective residence time teff based on t10/T |  |  | Chose chambers in series
| Effective residence time teff based on tm/T |  |  | Chose mixing condition
Chose a method to calculate the Ct-value by using the dropdown menu (placing the arrow in the gray cell brings up the dropdown menu):
| Method to determine the IC and k |  | through model calculation (Cdose, TOC)
Calculated values
| IC (initial consumption) * | mg O3/l | #DIV/0!
| Cin | mg O3/l | #DIV/0!
| k (degradation constant) |  | #DIV/0!
| Ct-value | mg*min/l | #DIV/0! | (teff based on t10/T)
Note: A separate Ct-value for contact volume and reaction volume is not calculated here
Log-credit for ozone disinfection before potential deductions
|  |  | Bacteria | Virus | Giardia | Cryptosporidium
| Maximum log-credit |  | 4 | 4 | 3 | 3
| Calculated inactivation degree (log-reduction) |  | 0 | 0 | 0 | 0
| Used log-credit before deduction |  | 0 | 0 | 0 | 0
Deduction (in %) of the Ct-calculated (or maximum) log-reduction because of safety breaches in chemical disinfection plants as well as credit (in % of log-reduction) for safety actions actually implemented (Table 3.7):
A | Action at temporary dosing failure | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 10% |  |  | 0 | 0 | 0 | 0
A1 | Automatic shutdown of all water production | 10% | YES | 10% | 0 | 0 | 0 | 0
A2 | Alarm and automatic start of dosing equipment in reserve | 5% | YES | 5% | 0 | 0 | 0 | 0
Maximum deduction in category A: |  |  |  |  | 0 | 0 | 0 | 0
B | Action to reduce risk of dosing failure | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 15% |  |  | 0 | 0 | 0 | 0
B1 | Back-up generator and/or UPS installed | 10% | YES | 10% | 0 | 0 | 0 | 0
B2 | Reserve dosing equipment installed | 5% | NO | 0% | 0 | 0 | 0 | 0
B3 | Equalization volume that may satisfy the water need when water production is stopped at dosing failures | 10% | NO | 0% | 0 | 0 | 0 | 0
Maximum deduction in category B: |  |  |  |  | 0 | 0 | 0 | 0
C | Other actions | % of the Ct-calculated Log-reduction | Evaluation (Yes/No) | Influence on log reduction | Bacteria | Virus | Giardia | Cryptosporidium
| Lack of actions provides maximum deduction of: | 10% |  |  | 0 | 0 | 0 | 0
C1 | Satisfactory monitoring system installed | 5% | YES | 5% | 0 | 0 | 0 | 0
C2 | Storage of critical reserve equipment | 5% | NO | 0% | 0 | 0 | 0 | 0
C3 | Satisfactory routines for cleaning, control and calibration of sensors for monitoring of residual ozone | 5% | NO | 0% | 0 | 0 | 0 | 0
Maximum deduction in category C: |  |  |  |  | 0 | 0 | 0 | 0
Log-reduction when using ozone disinfection method: |  |  |  |  | Bacteria | Virus | Giardia | Cryptosporidium
Log-credit before deduction: |  |  |  |  | 0 | 0 | 0 | 0
Reduction in log-credit because or missing actions (A + B + C): |  |  |  |  | 0 | 0 | 0 | 0
Log-credit for ozone disinfection including deductions. Transfers to summary. |  |  |  |  | 0 | 0 | 0 | 0

## Summary
SUMMARY
Owner of water treatment plant: | BB
Name of the water treatment plant: | VV
Water treatment plants barrier status. Summary is based on previously filled out sheet (automatically transferred). |  |  | Bacteria | Virus | Parasites
[5 empty] | Giardia | Cryptosporidium
Necessary log reduction in final disinfection | A |  | 0 | 0 | 0 | 0 | Retrieved from Start sheet
Hygienic barriers before disinfection | B | Lakes and catchments areas log-credit | 0 | 0 | 0 | 0 | Retrieved from Lakes and catchments sheet
|  | Groundwater log-credit | 0 | 0 | 0 | 0 | Retrieved from Groundwater sheet
|  | Infiltration of surface water | 0 | 0 | 0 | 0 | Retrieved from Infiltration sheet
| C | Water treatment process 1 | 0 | 0 | 0 | 0 | Retrieved from Water treatment beyond disinfection (process 1) sheet
|  | Water treatment process 2 | 0 | 0 | 0 | 0 | Retrieved from Water treatment beyond disinfection (process 2) sheet
Necessary log reduction in final disinfection | D | D = A ÷ B ÷ C | 0 | 0 | 0 | 0
Effect of disinfection barriers | E | UV-disinfection | 0 | 0 | 0 | 0 | Retrieved from UV sheet
|  | Chlorine-disinfection | 0 | 0 | 0 | 0 | Retrieved from Chlorine sheet
|  | Chlorine dioxide-disinfection | 0 | 0 | 0 | 0 | Retrieved from Chlorine dioxide sheet
|  | Ozone-disinfection | 0 | 0 | 0 | 0 | Retrieved from Ozone sheet
Barrier status |  |  | 0 | 0 | 0 | 0 | Negative values show that the water treatment plant does not have sufficient barriers and that the measures must be implemented.

## tab 3.3 (hidden)
Maksimal log-kreditt for ulike tiltak i nye anlegg
Barrieretiltak | Bakterier | Virus | Parasitter
Tiltak knyttet til vannkilde og nedslagsfelt - innsjøer
Maksimal log-kreditt, hvorav | 3 | 3 | 2
Maksimal log-kreditt for fysiske og restriktive tiltak (3.4) | 3 | 3 | 2
Maksimal log-kreditt for overvåkingstiltak på råvann (3.8) | 1 | 1 | 0.75
Tiltak knyttet til vannkilde og nedslagsfelt - grunnvann
Maksimal log-kreditt for tiltak knyttet til løsmassebrønner, hvorav | 3 | 3 | 2
Maksimal log-kreditt for overvåkingstiltak på råvann | 1 | 1 | 0.75
Maksimal log-kreditt for tiltak knyttet til fjellbrønner, hvorav | 2 | 2 | 1.5
Maksimal log-kreditt for overvåkingstiltak på råvann | 1 | 1 | 0.75
Tiltak knyttet til vannkilde og nedslagsfelt - Elver og bekker
Maksimal log-kreditt knyttet til overvåkning av råvannskvalitet - forutsetter automatisk avstengning av råvannstilførsel fra aktuell kilde ved overskridelse av grenseverdi | 1 | 1 | 0.75
Vannbehandlingstiltak utover sluttdesinfeksjon
Maksimal log-kreditt for vannbehandling utover sluttdesinfeksjon | 3 | 3 | 3
Maksimal log-kreditt for driftsovervåkning vannbehandlingsanlegget | 1 | 1 | 0.75
Absolutt maksimalt oppnåelig log-kreditt gjennom tiltak både i vannkilde/nedslagsfelt og vannbehandling utover sluttdesinfeksjon
Med innsjøer som kilde | 6 | 6 | 4
Med grunnvann som kilde | 6 | 6 | 4
Løsmassebrønner | 6 | 6 | 4
Fjellbrønner | 5 | 5 | 3.5
Med elver og bekker som kilde | 4.5 | 4.5 | 3

## key (hidden)
YES
NO
Valg av desinfeksjonsmetode UV
| Bacteria |  | Virus |  | Parasites
Choose category |  | Choose category |  | Choose category
Does not have UV disinfection | 0 | Does not have UV disinfection | 0 | Does not have UV disinfection | 0
40 mJ/cm2 biodosimetric dose excl. Adenovirus | 4 | 40 mJ/cm2 biodosimetric dose excl. Adenovirus | 3.5 | 40 mJ/cm2 biodosimetric dose excl. Adenovirus | 4
40 mJ/cm2 biodosimetric dose based on Adenovirus | 4 | 40 mJ/cm2 biodosimetric dose based on Adenovirus | 1.25 | 40 mJ/cm2 biodosimetric dose based on Adenovirus | 4
30 mJ/cm2 average dose excl. Adenovirus | 3 | 30 mJ/cm2 average dose excl. Adenovirus | 2.5 | 30 mJ/cm2 average dose excl. Adenovirus | 3
30 mJ/cm2 average dose based on Adenovirus | 3 | 30 mJ/cm2 average dose based on Adenovirus | 0.75 | 30 mJ/cm2 average dose based on Adenovirus | 3
30 mJ/cm2 biodosimetric dose excl. Adenovirus | 3.5 | 30 mJ/cm2 biodosimetric dose excl. Adenovirus | 3 | 30 mJ/cm2 biodosimetric dose excl. Adenovirus | 3.5
30 mJ/cm2 biodosimetric dose based on Adenovirus | 3.5 | 30 mJ/cm2 biodosimetric dose based on Adenovirus | 1 | 30 mJ/cm2 biodosimetric dose based on Adenovirus | 3.5
25 mJ/cm2 biodosimetric dose excl. Adenovirus | 3 | 25 mJ/cm2 biodosimetric dose excl. Adenovirus | 2.5 | 25 mJ/cm2 biodosimetric dose excl. Adenovirus | 3
25 mJ/cm2 biodosimetric dose based on Adenovirus | 3 | 25 mJ/cm2 biodosimetric dose based on Adenovirus | 0.75 | 25 mJ/cm2 biodosimetric dose based on Adenovirus | 3
X
Tabele 3.1 Required Ct-values (mg min/l) for inactivation of bacteria, virus and parasites
Bacteria |  | Viruses |  | Parasites of the Giardia group |  | Parasites of the Cryptosporidium group
Does not disinfect with chlorine | 0 | Does not disinfect with chlorine | 0 | Does not disinfect with chlorine | 0 | Does not disinfect with chlorine | 0
pH < 7 and temperature 4ºC | 1 | pH < 7 and temperature 4ºC | 4 | pH < 7 and temperature 4ºC | 75 | pH < 7 and temperature 4ºC | 1000
pH 7 - 8 and temperature 4ºC | 1.5 | pH 7 - 8 and temperature 4ºC | 6 | pH 7 - 8 and temperature 4ºC | 100 | pH 7 - 8 and temperature 4ºC | 1000
pH > 8 and temperature 4ºC | 2 | pH > 8 and temperature 4ºC | 8 | pH > 8 and temperature 4ºC | 175 | pH > 8 and temperature 4ºC | 1000
pH < 7 and temperature 0,5ºC | 1.5 | pH < 7 and temperature 0,5ºC | 6 | pH < 7 and temperature 0,5ºC | 100 | pH < 7 and temperature 0,5ºC | 1000
pH 7 - 8 and temperature 0,5ºC | 2 | pH 7 - 8 and temperature 0,5ºC | 9 | pH 7 - 8 and temperature 0,5ºC | 150 | pH 7 - 8 and temperature 0,5ºC | 1000
pH > 8 and temperature 0,5ºC | 3 | pH > 8 and temperature 0,5ºC | 12 | pH > 8 and temperature 0,5ºC | 250 | pH > 8 and temperature 0,5ºC | 1000
Tabele 3.1 Required Ct-values (mg min/l) for inactivation of bacteria, virus and parasites
Bacteria |  | Viruses |  | Parasites of the Giardia group |  | Parasites of the Cryptosporidium group
Does not disinfect with chlorine dioxide | 0 | Does not disinfect with chlorine dioxide | 0 | Does not disinfect with chlorine dioxide | 0 | Does not disinfect with chlorine dioxide | 0
Chlorine dioxide and temperature 4ºC | 1 | Chlorine dioxide and temperature 4ºC | 10 | Chlorine dioxide and temperature 4ºC | 20 | Chlorine dioxide and temperature 4ºC | 100
Chlorine dioxide and temperature 0,5ºC | 1.5 | Chlorine dioxide and temperature 0,5ºC | 15 | Chlorine dioxide and temperature 0,5ºC | 30 | Chlorine dioxide and temperature 0,5ºC | 150
Table 3.1 Required Ct-values (mg min/l) for inactivation of bacteria, virus and parasites
Bacteria |  | Viruses |  | Parasites of the Giardia group |  | Parasites of the Cryptosporidium group
Does not disinfect with ozone | 0 | Does not disinfect with ozone | 0 | Does not disinfect with ozone | 0 | Does not disinfect with ozone | 0
Ozone and temperature 4ºC | 0.5 | Ozone and temperature 4ºC | 1 | Ozone and temperature 4ºC | 1.5 | Ozone and temperature 4ºC | 30
Ozone and temperature 0,5ºC | 0.75 | Ozone and temperature 0,5ºC | 1.4 | Ozone and temperature 0,5ºC | 2 | Ozone and temperature 0,5ºC | 45
Determination of initial consumption (IC) and degredation constant (k):
by measurements (Cdose, Cin og Cout)
through model calculation (Cdose, TOC)
through a combination of measurements and calculations (Cdose, Cout og TOC)

## key 2 (hidden)
Tabell 3.2 Veiledende verdier for hydraulisk faktor (t10/T). Sett kryss ved grad av stempelstrømning og kammerløsning
Grad av stempelstrøm | Hydraulisk faktor Fh1.2 |  |  | Serie faktor Fs
Kamre i serie
| t10/T1 | tm/T2 |  | 1 |  | 2 |  | 3
Ingen (ideell blanding) | 0.1 | 0.3 | Ingen (ideell blanding) | 1 | Ingen (ideell blanding) | 2 | Ingen (ideell blanding) | 2.5
Dårlig | 0.3 | 0.4 | Dårlig | 1 | Dårlig | 1.8 | Dårlig | 2
Middels | 0.5 | 0.4 | Middels | 1 | Middels | 1.5 | Middels | 1.8
Ganske bra | 0.7 | 0.7 | Ganske bra | 1 | Ganske bra | 1.3 | Ganske bra | 1.4
Svært bra | 0.9 | 0.9 | Svært bra | 1 | Svært bra | 1.1 | Svært bra | 1.1
Perfekt (stempelstrøm) | 1 | 1 | Perfekt (stempelstrøm) | 1 | Perfekt (stempelstrøm) | 1 | Perfekt (stempelstrøm) | 1
1Faktor som som t10/T multipliseres med når man har hhv. 2 og 3 kammer i serie i kontaktbassenget